## IO List - Tagsight Export
Tag Number | Service Description | Instrument Type | Signal Class | Range / Units | Confidence % | P&ID Sheet | Notes
FIT-101 | Feed Water Flow to Reactor R-101 | Flow Transmitter | AI | 0-500 m³/h | 97 | PID-001
PIT-102 | Reactor R-101 Inlet Pressure | Pressure Transmitter | AI | 0-25 barg | 95 | PID-001
TT-103A | Reactor R-101 Top Temperature | Temperature Transmitter | AI | 0-400 °C | 98 | PID-001 | Redundant pair A
TT-103B | Reactor R-101 Top Temperature | Temperature Transmitter | AI | 0-400 °C | 96 | PID-001 | Redundant pair B
LIT-104 | Reactor R-101 Level | Level Transmitter | AI | 0-100 % | 94 | PID-001 | Guided wave radar
AT-105 | Reactor R-101 Outlet pH | Analyzer Transmitter | AI | 0-14 pH | 91 | PID-002
FIT-201 | Distillation Column D-201 Feed Flow | Flow Transmitter | AI | 0-200 m³/h | 96 | PID-003 | Coriolis type
TT-202 | D-201 Overhead Vapor Temperature | Temperature Transmitter | AI | 0-250 °C | 93 | PID-003
PIT-203 | D-201 Column Pressure | Pressure Transmitter | AI | 0-10 barg | 97 | PID-003
LIT-204 | D-201 Reflux Drum V-202 Level | Level Transmitter | AI | 0-100 % | 78 | PID-003 | Tag partially obscured on drawing
FCV-106 | Reactor R-101 Feed Control Valve | Control Valve | AO | 4-20 mA | 95 | PID-001 | Fail-closed
TCV-107 | Reactor R-101 Coolant Control Valve | Control Valve | AO | 4-20 mA | 92 | PID-002 | Fail-open
PCV-205 | D-201 Pressure Control Valve | Control Valve | AO | 4-20 mA | 94 | PID-003
FCV-206 | D-201 Reflux Flow Control Valve | Control Valve | AO | 4-20 mA | 97 | PID-003
LCV-207 | D-201 Bottoms Level Control Valve | Control Valve | AO | 4-20 mA | 88 | PID-004
PSH-108 | Reactor R-101 High Pressure Switch | Pressure Switch | DI | Trip @ 22 barg | 96 | PID-001 | SIL 2 rated
LSLL-109 | Reactor R-101 Low-Low Level Switch | Level Switch | DI | Trip @ 10 % | 93 | PID-001 | Interlock I-101
TSH-110 | Reactor R-101 High Temperature Switch | Temperature Switch | DI | Trip @ 380 °C | 72 | PID-002 | Tag number unclear - verify
FSL-208 | D-201 Reflux Pump P-202 Low Flow Switch | Flow Switch | DI | Trip @ 15 m³/h | 89 | PID-004
ZSC-301 | Emergency Vent Valve XV-301 Closed Position | Limit Switch | DI | Open/Closed | 95 | PID-005
XV-111 | Reactor R-101 Feed Shutoff Valve | Shutoff Valve | DO | Open/Close | 97 | PID-001 | Fail-closed, SIL 2
XV-112 | Reactor R-101 Emergency Vent Valve | Shutoff Valve | DO | Open/Close | 94 | PID-002 | Fail-open
SV-113 | Reactor R-101 N2 Purge Solenoid | Solenoid Valve | DO | Energize/De-energize | 76 | PID-002 | Possible misread - confirm SV vs XV
XV-209 | D-201 Feed Isolation Valve | Shutoff Valve | DO | Open/Close | 93 | PID-003
YA-302 | Emergency Shutdown Alarm Horn | Annunciator | DO | On/Off | 91 | PID-005 | Area alarm
SUMMARY
Total Instruments | 25
Signal Class Breakdown | AI: 10 ¦ AO: 5 ¦ DI: 5 ¦ DO: 5

## Export Info
Exported by | Tagsight
Export date | 2026-04-02
Source | Sample P&ID - Chemical Processing Unit
ISA Standard | ISA 5.1
Version | 1.0
Total Instruments | 25
Analog Inputs (AI) | 10
Analog Outputs (AO) | 5
Digital Inputs (DI) | 5
Digital Outputs (DO) | 5